## Read this first
Company name: | Horizon Power
Electricity Compliance Manual Datasheet - Distribution Indicators 2016/17
IMPORTANT NOTICE FOR ELECTRICITY DISTRIBUTION LICENSEES
Licensees should refer to the Electricity Distribution Licence Performance Reporting Handbook for information on the definitions of electricity distribution indicators, listed in these datasheets.

## Network Reliability
Distributor: Horizon Power
Reporting Period: 2016/17
Network Reliability
Indicator No. | Reference | Description |  |  | Basis of Reporting |  | Comments
[5 empty] | Number | Percentage
NQR 1 | Electricity Industry (Network Quality and Reliability of Supply) Code Sch 1(5), item 5 | The number of premises of small use customers to which the supply of electricity has been interrupted for more than 12 hours continuously |  |  | REFER TABLE 1 (below)
NQR 2 | Electricity Industry (Network Quality and Reliability of Supply) Code Sch 1(5), item 5 | The number of premises of small use customers to which the supply of electricity has been interrupted more than the permitted number of times, as is defined in section 12(1) {of the NQ&R Code} |  |  | REFER TABLE 1 (below)
NQR 3 | Electricity Industry (Network Quality and Reliability of Supply) Code Sch 1(11)(a), item 11(a) | For each discrete area, the average length of interruption of supply to customer premises expressed in minutes |  |  | 103.42
NQR 4 | Electricity Industry (Network Quality and Reliability of Supply) Code Sch 1(11)(b), item 11(b) | For each discrete area, the average number of interruptions of supply to customer premises |  |  | 3.33
NQR 5 | Electricity Industry (Network Quality and Reliability of Supply) Code Sch 1(11)(c), item 11(c) | For each discrete area, the average percentage of time that electricity has been supplied to customer premises |  |  | 99.9841
NQR 6 | Electricity Industry (Network Quality and Reliability of Supply) Code Sch 1(11)(d), item 11(d) | For each discrete area, the average total length of all interruptions of supply to customer premises expressed in minutes |  |  | 338.4515
NQR 7 | SCONRRR | Overall SAIDI by Total Network, CBD, Urban, Short Rural and Long Rural |  |  | REFER TABLE 2 (below)
NQR 8 | SCONRRR | Distribution Network (Planned) SAIDI by Total Network, CBD, Urban, Short Rural and Long Rural |  |  | REFER TABLE 2 (below)
NQR 9 | SCONRRR | Distribution Network (Unplanned) SAIDI by Total Network, CBD, Urban, Short Rural and Long Rural |  |  | REFER TABLE 2 (below)
NQR 10 | SCONRRR | Normalised distribution network SAIDI by Total Network, CBD, Urban, Short Rural and Long Rural |  |  | REFER TABLE 2 (below)
NQR 11 | SCONRRR | Overall SAIFI by Total Network, CBD, Urban, Short Rural and Long Rural |  |  | REFER TABLE 2 (below)
NQR 12 | SCONRRR | Distribution Network (Planned) SAIFI by Total Network, CBD, Urban, Short Rural and Long Rural |  |  | REFER TABLE 2 (below)
NQR 13 | SCONRRR | Distribution Network (Unplanned) SAIFI by Total Network, CBD, Urban, Short Rural and Long Rural |  |  | REFER TABLE 2 (below)
NQR 14 | SCONRRR | Normalised distribution network SAIFI by Total Network, CBD, Urban, Short Rural and Long Rural |  |  | REFER TABLE 2 (below)
NQR 15 | SCONRRR | Overall CAIDI by Total Network, CBD, Urban, Short Rural and Long Rural |  |  | REFER TABLE 2 (below)
NQR 16 | SCONRRR | Distribution Network (Planned) CAIDI by Total Network, CBD, Urban, Short Rural and Long Rural |  |  | REFER TABLE 2 (below)
NQR 17 | SCONRRR | Distribution Network (Unplanned) CAIDI by Total Network, CBD, Urban, Short Rural and Long Rural |  |  | REFER TABLE 2 (below)
NQR 18 | SCONRRR | Normalised distribution network CAIDI by Total Network, CBD, Urban, Short Rural and Long Rural |  |  | REFER TABLE 2 (below)
NQ&R - Network Reliability - Table 1
Description |  | Discrete Area |  | Total Network | Perth CBD and the urban areas combined | Other areas of the State | Comments
Interruptions for more than 12 hours continuously (Sch 1 section 5(a) NQ&R Code) |  | Number of premises interrupted |  | 1663
|  | Number of interruptions |  | 190
More than the permitted number of interruptions (Sch 1 section 5(b) NQ&R Code) |  | Premises interrupted more than 9 times in a year |  |  | N/A
|  | Premises interrupted more than 16 times in a year |  |  |  | 101
SCONRRR - Network Reliability - Table 2
Description | Discrete Area |  | Total Network | CBD | Urban | Short Rural | Long Rural | Comments
SAIDI | Overall |  | 233.2942 | N/A | 2.3936 | 209.3193 | 846.4004 | There was a recalculation of Urban Feeder Criteria after Pilbara Underground Project. A number of feeders changed classification from Urban to Short Rural and a number of new feeders were classified as Urban.
| Distribution Network (Planned) |  | 67.0562 | N/A | 2.0407 | 59.27 | 261.8338
| Distribution Network (Unplanned) |  | 166.238 | N/A | 0.3529 | 150.0493 | 584.5666
| Normalised Distribution Network |  | 125.2373 | N/A | 0 | 106.9893 | 572.0423
SAIFI | Overall |  | 2.5569 | N/A | 0.013017 | 2.3402 | 8.2849
| Distribution Network (Planned) |  | 0.3874 | N/A | 0.010124 | 0.35878 | 1.1583
| Distribution Network (Unplanned) |  | 2.1695 | N/A | 0.0028926 | 1.9814 | 7.1266
| Normalised Distribution Network |  | 2.1145 | N/A | 0 | 1.9256 | 7.0674
CAIDI | Overall |  | 91.2418 | N/A | 183.8889 | 89.4465 | 102.162
| Distribution Network (Planned) |  | 173.0939 | N/A | 201.5714 | 165.1999 | 226.0466
| Distribution Network (Unplanned) |  | 76.6257 | N/A | 122 | 75.7295 | 82.0264
| Normalised Distribution Network |  | 59.2284 | N/A | 0 | 55.5601 | 80.9414

## Complaints
Complaints
Indicator No. | Reference | Description |  | Basis of Reporting |  |  | Comments
|  |  |  | Number | Percentage | Value ($)
NQR 19 | Electricity Industry (Network Quality and Reliability of Supply) Code Sch 1(6) | Total number of complaints received {that Part 2 or an instrument made under section 14(3) of the NQ&R Code has not been, or is not being, complied with} |  | 111 (41) |  |  | Horizon Power had an initiative to identify Neutral Integrity issues on the network. Initially, the criteria was very strict. Consequently a high number of Power Quality Investigations were raised internally as opposed to Customer raised Power Quality Complaints. This resulted in a spike in the number of Power Quality Investigations during February and March. The process was refined in April resulting in the normalisation of the quantity of Power Quality Investigations. The number in brackets is the number of Customer raised Power Quality Complaints.
NQR 20 | Electricity Industry (Network Quality and Reliability of Supply) Code clause Sch 1(7) | Total number of complaints received from customers in each of the discrete areas {that Part 2 or an instrument made under section 14(3) of the NQ&R Code has not been, or is not being, complied with} |  | REFER TABLE 3 (below)
NQR 21 | Electricity Industry (Network Quality and Reliability of Supply) Code clause Sch 1(8) | Total amount spent in addressing complaints {that Part 2 or an instrument made under section 14(3) of the NQ&R Code has not been, or is not being, complied with} other than by way of payment under sections 18 and 19 {of the NQ&R Code} |  |  |  | 1647756
NQR 22 | SCONRRR | Total number of technical QoS complaints |  | 111 |  |  | Total number of Power Quality Incidents entered here so the percentage formulas will work.
NQR 23 | SCONRRR | Total number of technical QoS complaints that are low supply voltage complaints |  | 15 |  |  | Category = Low Volts
NQR 24 | SCONRRR | Percentage of technical QoS complaints that are low supply voltage complaints |  |  | 13.51%
NQR 25 | SCONRRR | Total number of technical QoS complaints that are voltage dip complaints |  | 0
NQR 26 | SCONRRR | Percentage of technical QoS complaints that are voltage dip complaints
NQR 27 | SCONRRR | Total number of technical QoS complaints that are voltage swell complaints |  | 0
NQR 28 | SCONRRR | Percentage of technical QoS complaints that are voltage swell complaints
NQR 29 | SCONRRR | Total number of technical QoS complaints that are voltage spike complaints |  | 0
NQR 30 | SCONRRR | Percentage of technical QoS complaints that are voltage spike complaints
NQR 31 | SCONRRR | Total number of technical QoS complaints that are waveform distortion complaints |  | 0
NQR 32 | SCONRRR | Percentage of technical QoS complaints that are waveform distortion complaints
NQR 33 | SCONRRR | Total number of technical QoS complaints that are TV or radio interference complaints |  | 2 |  |  | Category = TV Interference
NQR 34 | SCONRRR | Percentage of technical QoS complaints that are TV or radio interference complaints |  |  | 1.802%
NQR 35 | SCONRRR | Total number of technical QoS complaints that are noise from appliances complaints |  | 0
NQR 36 | SCONRRR | Percentage of technical QoS complaints that are noise from appliances complaints
NQR 37 | SCONRRR | Total number of technical QoS complaints that are other complaints |  | 94 |  |  | Category = (High Volts, Voltage Fluctuation, Reliability)
NQR 38 | SCONRRR | Percentage of technical QoS complaints that are other complaints |  |  | 84.68% |  | Corrected Formula. Previously dividing by $F$10
NQR 39 | SCONRRR | Breakdown of technical QoS complaints into the likely cause of problem that caused the complaint separated into:
|  | Network equipment faulty - Total Number |  | 32 |  |  | Cause = Equipment Failure
|  | Network equipment faulty - Percentage |  |  | 28.83%
|  | Network interference by NSP equipment - Total Number |  | 0
Network interference by NSP equipment - Percentage
|  | Network interference by another customer - Total Number |  | 0
Network interference by another customer - Percentage
|  | Network limitation - Total Number |  | 0
Network limitation - Percentage
|  | Customer internal problem - Total Number |  | 0
Customer internal problem - Percentage
|  | No problem identified - Total Number |  | 59 |  |  | Cause = (PQI, Unknown)
|  | No problem identified - Percentage |  |  | 53.15%
|  | Environmental - Total Number |  | 9 |  |  | Cause = (Bird, Insect, Lightning)
|  | Environmental - Percentage |  |  | 8.108%
|  | Other - Total Number |  | 11 |  |  | Cause = (Human Error, Planned Outage, PQI, Wind)
|  | Other - Percentage |  |  | 9.91%
NQ&R - Complaints - Table 3
Discrete Area |  | Number of Complaints Received | Comments
Perth CBD |  | N/A
Urban areas other than the Perth CBD |  | N/A
All other areas of the State |  | 111 (41) | Horizon Power had an initiative to identify Neutral Integrity issues on the network. Initially, the criteria was very strict. Consequently a high number of Power Quality Investigations were raised internally as opposed to Customer raised Power Quality Complaints. This resulted in a spike in the number of Power Quality Investigations during February and March. The process was refined in April resulting in the normalisation of the quantity of Power Quality Investigations. The number in brackets is the number of Customer raised Power Quality Complaints.

## Compensation Payments
Compensation Payments
Indicator No. | Reference | Description | Basis of Reporting |  |  | Comments
|  |  | Number | Percentage | Value ($)
NQR 40 | Electricity Industry (Network Quality and Reliability of Supply) Code clause Sch 1(9) | The number of payments made, and the total amount paid under section 18 of the NQ&R Code | 1 |  | 20
NQR 41 | Electricity Industry (Network Quality and Reliability of Supply) Code clause Sch 1(9) | The number of payments made, and the total amount paid under section 19 of the NQ&R Code | 346 |  | 27680 | There were 3 major outages greater than 12 hours as listed below. • Fitzroy Crossing (Fire) • Yungngora (Flooding) • Karratha (Blown Ring Main Unit)

## Network & Asset Info
Network and Asset Information
Indicator No | Reference | Description |  |  | Basis of Reporting |  | Comments
[5 empty] | Number | Percentage
NQR 42 | SCONRRR | Number of metered supply points by feeder category (CBD, urban, short rural and long rural), reported against the categories of residential and non-residential customers and sub-transmission, high voltage and low voltage |  |  | REFER TABLE 4A (below)
NQR 43 | SCONRRR | Number of unmetered supply points, by type of feeder (CBD, urban, long rural and short rural) |  |  | REFER TABLE 4B (below)
NQR 44 | SCONRRR | Energy delivered (GWh) by type of feeder (CBD, urban, long rural and short rural) reported against the categories of residential and non-residential customers and sub-transmission, high voltage and low voltage |  |  | REFER TABLE 4C (below)
NQR 45 | SCONRRR | Line lengths by type of feeder (CBD, urban, long rural and short rural) reported against the categories of underground and overhead line categories and sub-transmission, high voltage and low voltage |  |  | REFER TABLE 5A (below)
NQR 46 | SCONRRR | Number and total capacity of transformers, separated into sub-transmission and distribution |  |  | REFER TABLE 5B (below)
NQR 47 | SCONRRR | Total distribution losses (%) |  |  |  | N/A
NQR 48 | SCONRRR | Size of network service area (sq km) |  |  | N/A
NQR 49 | SCONRRR | Number of poles |  |  | 57888 |  | Distribution 56,920 + Transmission 968
NQR 50 | SCONRRR | Peak demand (MW) |  |  | N/A
Network & Asset Information - Table 4A
Number of Metered Supply Points |  | Total No. | By type of customer |  | By supply voltage |  |  | Comments
Feeder Category |  |  | Residential | Non-residential | ST | HV | LV
CBD |  | N/A | N/A | N/A | N/A | N/A | N/A
Urban |  | 1501 | N/A | N/A | N/A | N/A | N/A | As at 30 June 2017. This year excluded UMS. This year excludes UMS.
Rural Short |  | 45135 | N/A | N/A | N/A | N/A | N/A | As at 30 June 2017. This year excluded UMS. This year excludes UMS.
Rural Long |  | 2112 | N/A | N/A | N/A | N/A | N/A | As at 30 June 2017. This year excluded UMS. This year excludes UMS.
Network & Asset Information - Table 4B
Number of Un-metered Supply Points | [5 empty] | Comments
|  | CBD | Urban | Rural Short | Rural Long
Total No. |  | N/A | 21 | 424 | 23 | As at 30 June 2017. There was a recalculation of Urban Feeders
Network & Asset Information - Table 4C
Energy delivered (GWh) |  | By type of customer |  |  | By supply voltage |  |  | Comments
Feeder Category |  | Total GWh | Residential | Non-residential | ST | HV | LV
CBD |  | N/A | N/A | N/A | N/A | N/A | N/A
Urban |  | N/A | N/A | N/A | N/A | N/A | N/A
Rural Short |  | N/A | N/A | N/A | N/A | N/A | N/A
Rural Long |  | N/A | N/A | N/A | N/A | N/A | N/A
SCONRRR Business Descriptors - Table 5A
Line length (km) |  |  |  |  | By supply voltage |  |  | Comments
Feeder Category |  | Total km | Underground | Overhead | ST | HV | LV
CBD |  | N/A | N/A | N/A | N/A | N/A | N/A
Urban |  | 146.9033 | 145.2548 | 1.6486 | N/A | 63.8647 | 83.0386 | As at 30 June 2017
Rural Short |  | 4422.68 | 2235.07 | 2187.6 | N/A | 2406.62 | 2016.06 | As at 30 June 2017
Rural Long |  | 3311.6647 | 54.1361 | 3257.5285 | N/A | 3252.8804 | 58.7843 | As at 30 June 2017
SCONRRR Business Descriptors - Table 5B
Transfomer Type |  | Number of Transformers | Total capacity of Transformers (MVA) |  | Comments
Sub-transmission |  | N/A | N/A
Distribution |  | 4421 | 801 MVA |  | As at 30 June 2017